## 32ede
keyname | device obj.-instance | object-name | object-type | object-instance | description | present-value-default | min-present-value | max-present-value | settable | supports COV | hi-limit | low-limit | state-text-reference | unit-code | vendor-specific-addres
OBJECT_ANALOG_INPUT:0 | 47818 |  | 0 | 0
OBJECT_BINARY_VALUE:116 | 47818 | Z1_MY_POSITION_BV | 5 | 116 | Recalls the pre-defined position/angle
OBJECT_BINARY_VALUE:216 | 47818 | Z2_MY_POSITION_BV | 5 | 216 | Recalls the pre-defined position/angle
OBJECT_BINARY_VALUE:316 | 47818 | Z3_MY_POSITION_BV | 5 | 316 | Recalls the pre-defined position/angle
OBJECT_BINARY_VALUE:416 | 47818 | Z4_MY_POSITION_BV | 5 | 416 | Recalls the pre-defined position/angle
OBJECT_BINARY_VALUE:516 | 47818 | Z5_MY_POSITION_BV | 5 | 516 | Recalls the pre-defined position/angle
OBJECT_BINARY_VALUE:616 | 47818 | Z6_MY_POSITION_BV | 5 | 616 | Recalls the pre-defined position/angle
OBJECT_BINARY_VALUE:716 | 47818 | Z7_MY_POSITION_BV | 5 | 716 | Recalls the pre-defined position/angle
OBJECT_BINARY_VALUE:816 | 47818 | Z8_MY_POSITION_BV | 5 | 816 | Recalls the pre-defined position/angle
OBJECT_BINARY_VALUE:102 | 47818 | Z1_ERROR_BV | 5 | 102 | Shows critical defect of wind sensor, wind direction sensor and Outside Sensor Box
OBJECT_BINARY_VALUE:202 | 47818 | Z2_ERROR_BV | 5 | 202 | Shows critical defect of wind sensor, wind direction sensor and Outside Sensor Box
OBJECT_BINARY_VALUE:302 | 47818 | Z3_ERROR_BV | 5 | 302 | Shows critical defect of wind sensor, wind direction sensor and Outside Sensor Box
OBJECT_BINARY_VALUE:402 | 47818 | Z4_ERROR_BV | 5 | 402 | Shows critical defect of wind sensor, wind direction sensor and Outside Sensor Box
OBJECT_BINARY_VALUE:502 | 47818 | Z5_ERROR_BV | 5 | 502 | Shows critical defect of wind sensor, wind direction sensor and Outside Sensor Box
OBJECT_BINARY_VALUE:602 | 47818 | Z6_ERROR_BV | 5 | 602 | Shows critical defect of wind sensor, wind direction sensor and Outside Sensor Box
OBJECT_BINARY_VALUE:702 | 47818 | Z7_ERROR_BV | 5 | 702 | Shows critical defect of wind sensor, wind direction sensor and Outside Sensor Box
OBJECT_BINARY_VALUE:802 | 47818 | Z8_ERROR_BV | 5 | 802 | Shows critical defect of wind sensor, wind direction sensor and Outside Sensor Box
OBJECT_ANALOG_INPUT:3 | 47818 | SUN_1_AI | 0 | 3 | Shows current brightness value
OBJECT_ANALOG_INPUT:4 | 47818 | SUN_2_AI | 0 | 4 | Shows current brightness value
OBJECT_ANALOG_INPUT:5 | 47818 | SUN_3_AI | 0 | 5 | Shows current brightness value
OBJECT_ANALOG_INPUT:6 | 47818 | SUN_4_AI | 0 | 6 | Shows current brightness value
OBJECT_ANALOG_INPUT:7 | 47818 | SUN_5_AI | 0 | 7 | Shows current brightness value
OBJECT_ANALOG_INPUT:8 | 47818 | SUN_6_AI | 0 | 8 | Shows current brightness value
OBJECT_ANALOG_INPUT:9 | 47818 | SUN_7_AI | 0 | 9 | Shows current brightness value
OBJECT_ANALOG_INPUT:10 | 47818 | SUN_8_AI | 0 | 10 | Shows current brightness value
OBJECT_ANALOG_INPUT:12 | 47818 | 1_INSIDE_TEMPERATURE_AI | 0 | 12 | Shows current inside temperature value
OBJECT_ANALOG_INPUT:13 | 47818 | 2_INSIDE_TEMPERATURE_AI | 0 | 13 | Shows current inside temperature value
OBJECT_ANALOG_INPUT:14 | 47818 | 3_INSIDE_TEMPERATURE_AI | 0 | 14 | Shows current inside temperature value
OBJECT_ANALOG_INPUT:15 | 47818 | 4_INSIDE_TEMPERATURE_AI | 0 | 15 | Shows current inside temperature value
OBJECT_ANALOG_INPUT:11 | 47818 | OUTSIDE_TEMPERATURE_AI | 0 | 11 | Shows current outside temperature value
OBJECT_BINARY_INPUT:0 | 47818 | PRECIPITATION_BI | 3 | 0 | Shows current precipitation value
OBJECT_ANALOG_INPUT:2 | 47818 | WIND_DIRECTION_AI | 0 | 2 | Shows current wind direction value
OBJECT_ANALOG_INPUT:1 | 47818 | WIND_SPEED_2_AI | 0 | 1 | Shows current wind speed value
OBJECT_BINARY_VALUE:104 | 47818 | Z1_SNOW_FROST_ICE_RAIN_BV | 5 | 104 | Shows if snow, frost, ice or rain is active due to exceeded on delay time, precipitation and temperature
OBJECT_BINARY_VALUE:204 | 47818 | Z2_SNOW_FROST_ICE_RAIN_BV | 5 | 204 | Shows if snow, frost, ice or rain is active due to exceeded on delay time, precipitation and temperature
OBJECT_BINARY_VALUE:304 | 47818 | Z3_SNOW_FROST_ICE_RAIN_BV | 5 | 304 | Shows if snow, frost, ice or rain is active due to exceeded on delay time, precipitation and temperature
OBJECT_BINARY_VALUE:404 | 47818 | Z4_SNOW_FROST_ICE_RAIN_BV | 5 | 404 | Shows if snow, frost, ice or rain is active due to exceeded on delay time, precipitation and temperature
OBJECT_BINARY_VALUE:504 | 47818 | Z5_SNOW_FROST_ICE_RAIN_BV | 5 | 504 | Shows if snow, frost, ice or rain is active due to exceeded on delay time, precipitation and temperature
OBJECT_BINARY_VALUE:604 | 47818 | Z6_SNOW_FROST_ICE_RAIN_BV | 5 | 604 | Shows if snow, frost, ice or rain is active due to exceeded on delay time, precipitation and temperature
OBJECT_BINARY_VALUE:704 | 47818 | Z7_SNOW_FROST_ICE_RAIN_BV | 5 | 704 | Shows if snow, frost, ice or rain is active due to exceeded on delay time, precipitation and temperature
OBJECT_BINARY_VALUE:804 | 47818 | Z8_SNOW_FROST_ICE_RAIN_BV | 5 | 804 | Shows if snow, frost, ice or rain is active due to exceeded on delay time, precipitation and temperature
OBJECT_BINARY_VALUE:100 | 47818 | Z1_ALARM_BV | 5 | 100 | Shows status of external alarm input
OBJECT_BINARY_VALUE:200 | 47818 | Z2_ALARM_BV | 5 | 200 | Shows status of external alarm input
OBJECT_BINARY_VALUE:300 | 47818 | Z3_ALARM_BV | 5 | 300 | Shows status of external alarm input
OBJECT_BINARY_VALUE:400 | 47818 | Z4_ALARM_BV | 5 | 400 | Shows status of external alarm input
OBJECT_BINARY_VALUE:500 | 47818 | Z5_ALARM_BV | 5 | 500 | Shows status of external alarm input
OBJECT_BINARY_VALUE:600 | 47818 | Z6_ALARM_BV | 5 | 600 | Shows status of external alarm input
OBJECT_BINARY_VALUE:700 | 47818 | Z7_ALARM_BV | 5 | 700 | Shows status of external alarm input
OBJECT_BINARY_VALUE:800 | 47818 | Z8_ALARM_BV | 5 | 800 | Shows status of external alarm input
OBJECT_BINARY_VALUE:106 | 47818 | Z1_MANUAL_BV | 5 | 106 | Shows that a manual command is executed
OBJECT_BINARY_VALUE:206 | 47818 | Z2_MANUAL_BV | 5 | 206 | Shows that a manual command is executed
OBJECT_BINARY_VALUE:306 | 47818 | Z3_MANUAL_BV | 5 | 306 | Shows that a manual command is executed
OBJECT_BINARY_VALUE:406 | 47818 | Z4_MANUAL_BV | 5 | 406 | Shows that a manual command is executed
OBJECT_BINARY_VALUE:506 | 47818 | Z5_MANUAL_BV | 5 | 506 | Shows that a manual command is executed
OBJECT_BINARY_VALUE:606 | 47818 | Z6_MANUAL_BV | 5 | 606 | Shows that a manual command is executed
OBJECT_BINARY_VALUE:706 | 47818 | Z7_MANUAL_BV | 5 | 706 | Shows that a manual command is executed
OBJECT_BINARY_VALUE:806 | 47818 | Z8_MANUAL_BV | 5 | 806 | Shows that a manual command is executed
OBJECT_BINARY_VALUE:107 | 47818 | Z1_TIMER_BV | 5 | 107 | Shows that an order is sent for a pre-defined time or period
OBJECT_BINARY_VALUE:207 | 47818 | Z2_TIMER_BV | 5 | 207 | Shows that an order is sent for a pre-defined time or period
OBJECT_BINARY_VALUE:307 | 47818 | Z3_TIMER_BV | 5 | 307 | Shows that an order is sent for a pre-defined time or period
OBJECT_BINARY_VALUE:407 | 47818 | Z4_TIMER_BV | 5 | 407 | Shows that an order is sent for a pre-defined time or period
OBJECT_BINARY_VALUE:507 | 47818 | Z5_TIMER_BV | 5 | 507 | Shows that an order is sent for a pre-defined time or period
OBJECT_BINARY_VALUE:607 | 47818 | Z6_TIMER_BV | 5 | 607 | Shows that an order is sent for a pre-defined time or period
OBJECT_BINARY_VALUE:707 | 47818 | Z7_TIMER_BV | 5 | 707 | Shows that an order is sent for a pre-defined time or period
OBJECT_BINARY_VALUE:807 | 47818 | Z8_TIMER_BV | 5 | 807 | Shows that an order is sent for a pre-defined time or period
OBJECT_BINARY_VALUE:105 | 47818 | Z1_LOCK_TIMER_BV | 5 | 105 | Shows that local control is locked for a pre-defined period
OBJECT_BINARY_VALUE:205 | 47818 | Z2_LOCK_TIMER_BV | 5 | 205 | Shows that local control is locked for a pre-defined period
OBJECT_BINARY_VALUE:305 | 47818 | Z3_LOCK_TIMER_BV | 5 | 305 | Shows that local control is locked for a pre-defined period
OBJECT_BINARY_VALUE:405 | 47818 | Z4_LOCK_TIMER_BV | 5 | 405 | Shows that local control is locked for a pre-defined period
OBJECT_BINARY_VALUE:505 | 47818 | Z5_LOCK_TIMER_BV | 5 | 505 | Shows that local control is locked for a pre-defined period
OBJECT_BINARY_VALUE:605 | 47818 | Z6_LOCK_TIMER_BV | 5 | 605 | Shows that local control is locked for a pre-defined period
OBJECT_BINARY_VALUE:705 | 47818 | Z7_LOCK_TIMER_BV | 5 | 705 | Shows that local control is locked for a pre-defined period
OBJECT_BINARY_VALUE:805 | 47818 | Z8_LOCK_TIMER_BV | 5 | 805 | Shows that local control is locked for a pre-defined period
OBJECT_BINARY_VALUE:101 | 47818 | Z1_LOCK_BV | 5 | 101 | Shows that local control is locked. Control via TouchBuco is still possible.
OBJECT_BINARY_VALUE:201 | 47818 | Z2_LOCK_BV | 5 | 201 | Shows that local control is locked. Control via TouchBuco is still possible.
OBJECT_BINARY_VALUE:301 | 47818 | Z3_LOCK_BV | 5 | 301 | Shows that local control is locked. Control via TouchBuco is still possible.
OBJECT_BINARY_VALUE:401 | 47818 | Z4_LOCK_BV | 5 | 401 | Shows that local control is locked. Control via TouchBuco is still possible.
OBJECT_BINARY_VALUE:501 | 47818 | Z5_LOCK_BV | 5 | 501 | Shows that local control is locked. Control via TouchBuco is still possible.
OBJECT_BINARY_VALUE:601 | 47818 | Z6_LOCK_BV | 5 | 601 | Shows that local control is locked. Control via TouchBuco is still possible.
OBJECT_BINARY_VALUE:701 | 47818 | Z7_LOCK_BV | 5 | 701 | Shows that local control is locked. Control via TouchBuco is still possible.
OBJECT_BINARY_VALUE:801 | 47818 | Z8_LOCK_BV | 5 | 801 | Shows that local control is locked. Control via TouchBuco is still possible.
OBJECT_BINARY_VALUE:112 | 47818 | Z1_SUN_PROTECTION_BV | 5 | 112 | Shows that the blinds are closed due to glare protection
OBJECT_BINARY_VALUE:212 | 47818 | Z2_SUN_PROTECTION_BV | 5 | 212 | Shows that the blinds are closed due to glare protection
OBJECT_BINARY_VALUE:312 | 47818 | Z3_SUN_PROTECTION_BV | 5 | 312 | Shows that the blinds are closed due to glare protection
OBJECT_BINARY_VALUE:412 | 47818 | Z4_SUN_PROTECTION_BV | 5 | 412 | Shows that the blinds are closed due to glare protection
OBJECT_BINARY_VALUE:512 | 47818 | Z5_SUN_PROTECTION_BV | 5 | 512 | Shows that the blinds are closed due to glare protection
OBJECT_BINARY_VALUE:612 | 47818 | Z6_SUN_PROTECTION_BV | 5 | 612 | Shows that the blinds are closed due to glare protection
OBJECT_BINARY_VALUE:712 | 47818 | Z7_SUN_PROTECTION_BV | 5 | 712 | Shows that the blinds are closed due to glare protection
OBJECT_BINARY_VALUE:812 | 47818 | Z8_SUN_PROTECTION_BV | 5 | 812 | Shows that the blinds are closed due to glare protection
OBJECT_BINARY_VALUE:108 | 47818 | Z1_BLOCK_HEAT_BV | 5 | 108 | Shows that the blinds are closed to avoid the room from overheating
OBJECT_BINARY_VALUE:208 | 47818 | Z2_BLOCK_HEAT_BV | 5 | 208 | Shows that the blinds are closed to avoid the room from overheating
OBJECT_BINARY_VALUE:308 | 47818 | Z3_BLOCK_HEAT_BV | 5 | 308 | Shows that the blinds are closed to avoid the room from overheating
OBJECT_BINARY_VALUE:408 | 47818 | Z4_BLOCK_HEAT_BV | 5 | 408 | Shows that the blinds are closed to avoid the room from overheating
OBJECT_BINARY_VALUE:508 | 47818 | Z5_BLOCK_HEAT_BV | 5 | 508 | Shows that the blinds are closed to avoid the room from overheating
OBJECT_BINARY_VALUE:608 | 47818 | Z6_BLOCK_HEAT_BV | 5 | 608 | Shows that the blinds are closed to avoid the room from overheating
OBJECT_BINARY_VALUE:708 | 47818 | Z7_BLOCK_HEAT_BV | 5 | 708 | Shows that the blinds are closed to avoid the room from overheating
OBJECT_BINARY_VALUE:808 | 47818 | Z8_BLOCK_HEAT_BV | 5 | 808 | Shows that the blinds are closed to avoid the room from overheating
OBJECT_BINARY_VALUE:110 | 47818 | Z1_MAINTAIN_HEAT_BV | 5 | 110 | Shows that the blinds are closed to prevent the room from cooling out
OBJECT_BINARY_VALUE:210 | 47818 | Z2_MAINTAIN_HEAT_BV | 5 | 210 | Shows that the blinds are closed to prevent the room from cooling out
OBJECT_BINARY_VALUE:310 | 47818 | Z3_MAINTAIN_HEAT_BV | 5 | 310 | Shows that the blinds are closed to prevent the room from cooling out
OBJECT_BINARY_VALUE:410 | 47818 | Z4_MAINTAIN_HEAT_BV | 5 | 410 | Shows that the blinds are closed to prevent the room from cooling out
OBJECT_BINARY_VALUE:510 | 47818 | Z5_MAINTAIN_HEAT_BV | 5 | 510 | Shows that the blinds are closed to prevent the room from cooling out
OBJECT_BINARY_VALUE:610 | 47818 | Z6_MAINTAIN_HEAT_BV | 5 | 610 | Shows that the blinds are closed to prevent the room from cooling out
OBJECT_BINARY_VALUE:710 | 47818 | Z7_MAINTAIN_HEAT_BV | 5 | 710 | Shows that the blinds are closed to prevent the room from cooling out
OBJECT_BINARY_VALUE:810 | 47818 | Z8_MAINTAIN_HEAT_BV | 5 | 810 | Shows that the blinds are closed to prevent the room from cooling out
OBJECT_BINARY_VALUE:109 | 47818 | Z1_SOLAR_HEATING_BV | 5 | 109 | Shows that the blinds are opened to take advantage of the sun
OBJECT_BINARY_VALUE:209 | 47818 | Z2_SOLAR_HEATING_BV | 5 | 209 | Shows that the blinds are opened to take advantage of the sun
OBJECT_BINARY_VALUE:309 | 47818 | Z3_SOLAR_HEATING_BV | 5 | 309 | Shows that the blinds are opened to take advantage of the sun
OBJECT_BINARY_VALUE:409 | 47818 | Z4_SOLAR_HEATING_BV | 5 | 409 | Shows that the blinds are opened to take advantage of the sun
OBJECT_BINARY_VALUE:509 | 47818 | Z5_SOLAR_HEATING_BV | 5 | 509 | Shows that the blinds are opened to take advantage of the sun
OBJECT_BINARY_VALUE:609 | 47818 | Z6_SOLAR_HEATING_BV | 5 | 609 | Shows that the blinds are opened to take advantage of the sun
OBJECT_BINARY_VALUE:709 | 47818 | Z7_SOLAR_HEATING_BV | 5 | 709 | Shows that the blinds are opened to take advantage of the sun
OBJECT_BINARY_VALUE:809 | 47818 | Z8_SOLAR_HEATING_BV | 5 | 809 | Shows that the blinds are opened to take advantage of the sun
OBJECT_BINARY_VALUE:111 | 47818 | Z1_COOLING_BV | 5 | 111 | Shows that the windows are opened to take advantage of the lower outside temperature
OBJECT_BINARY_VALUE:211 | 47818 | Z2_COOLING_BV | 5 | 211 | Shows that the windows are opened to take advantage of the lower outside temperature
OBJECT_BINARY_VALUE:311 | 47818 | Z3_COOLING_BV | 5 | 311 | Shows that the windows are opened to take advantage of the lower outside temperature
OBJECT_BINARY_VALUE:411 | 47818 | Z4_COOLING_BV | 5 | 411 | Shows that the windows are opened to take advantage of the lower outside temperature
OBJECT_BINARY_VALUE:511 | 47818 | Z5_COOLING_BV | 5 | 511 | Shows that the windows are opened to take advantage of the lower outside temperature
OBJECT_BINARY_VALUE:611 | 47818 | Z6_COOLING_BV | 5 | 611 | Shows that the windows are opened to take advantage of the lower outside temperature
OBJECT_BINARY_VALUE:711 | 47818 | Z7_COOLING_BV | 5 | 711 | Shows that the windows are opened to take advantage of the lower outside temperature
OBJECT_BINARY_VALUE:811 | 47818 | Z8_COOLING_BV | 5 | 811 | Shows that the windows are opened to take advantage of the lower outside temperature
OBJECT_BINARY_VALUE:103 | 47818 | Z1_WIND_BV | 5 | 103 | Shows that wind function is active due to exceeded wind threshold and on delay time
OBJECT_BINARY_VALUE:203 | 47818 | Z2_WIND_BV | 5 | 203 | Shows that wind function is active due to exceeded wind threshold and on delay time
OBJECT_BINARY_VALUE:303 | 47818 | Z3_WIND_BV | 5 | 303 | Shows that wind function is active due to exceeded wind threshold and on delay time
OBJECT_BINARY_VALUE:403 | 47818 | Z4_WIND_BV | 5 | 403 | Shows that wind function is active due to exceeded wind threshold and on delay time
OBJECT_BINARY_VALUE:503 | 47818 | Z5_WIND_BV | 5 | 503 | Shows that wind function is active due to exceeded wind threshold and on delay time
OBJECT_BINARY_VALUE:603 | 47818 | Z6_WIND_BV | 5 | 603 | Shows that wind function is active due to exceeded wind threshold and on delay time
OBJECT_BINARY_VALUE:703 | 47818 | Z7_WIND_BV | 5 | 703 | Shows that wind function is active due to exceeded wind threshold and on delay time
OBJECT_BINARY_VALUE:803 | 47818 | Z8_WIND_BV | 5 | 803 | Shows that wind function is active due to exceeded wind threshold and on delay time
OBJECT_DEVICE:47818 | 47818 | BGBC Besprechung | 8 | 47818 | This are the Properties of the TouchBuCo Bacnet.
OBJECT_BINARY_VALUE:117 | 47818 | Z1_LOCK_UNLOCK_BV | 5 | 117 | Write "1" to lock the local control
OBJECT_BINARY_VALUE:217 | 47818 | Z2_LOCK_UNLOCK_BV | 5 | 217 | Write "1" to lock the local control
OBJECT_BINARY_VALUE:317 | 47818 | Z3_LOCK_UNLOCK_BV | 5 | 317 | Write "1" to lock the local control
OBJECT_BINARY_VALUE:417 | 47818 | Z4_LOCK_UNLOCK_BV | 5 | 417 | Write "1" to lock the local control
OBJECT_BINARY_VALUE:517 | 47818 | Z5_LOCK_UNLOCK_BV | 5 | 517 | Write "1" to lock the local control
OBJECT_BINARY_VALUE:617 | 47818 | Z6_LOCK_UNLOCK_BV | 5 | 617 | Write "1" to lock the local control
OBJECT_BINARY_VALUE:717 | 47818 | Z7_LOCK_UNLOCK_BV | 5 | 717 | Write "1" to lock the local control
OBJECT_BINARY_VALUE:817 | 47818 | Z8_LOCK_UNLOCK_BV | 5 | 817 | Write "1" to lock the local control
OBJECT_BINARY_VALUE:115 | 47818 | Z1_DOWN_BV | 5 | 115 | Write "1" to send group to lower end limit
OBJECT_BINARY_VALUE:215 | 47818 | Z2_DOWN_BV | 5 | 215 | Write "1" to send group to lower end limit
OBJECT_BINARY_VALUE:315 | 47818 | Z3_DOWN_BV | 5 | 315 | Write "1" to send group to lower end limit
OBJECT_BINARY_VALUE:415 | 47818 | Z4_DOWN_BV | 5 | 415 | Write "1" to send group to lower end limit
OBJECT_BINARY_VALUE:515 | 47818 | Z5_DOWN_BV | 5 | 515 | Write "1" to send group to lower end limit
OBJECT_BINARY_VALUE:615 | 47818 | Z6_DOWN_BV | 5 | 615 | Write "1" to send group to lower end limit
OBJECT_BINARY_VALUE:715 | 47818 | Z7_DOWN_BV | 5 | 715 | Write "1" to send group to lower end limit
OBJECT_BINARY_VALUE:815 | 47818 | Z8_DOWN_BV | 5 | 815 | Write "1" to send group to lower end limit
OBJECT_BINARY_VALUE:113 | 47818 | Z1_UP_BV | 5 | 113 | Write "1" to send group to upper end limit
OBJECT_BINARY_VALUE:213 | 47818 | Z2_UP_BV | 5 | 213 | Write "1" to send group to upper end limit
OBJECT_BINARY_VALUE:313 | 47818 | Z3_UP_BV | 5 | 313 | Write "1" to send group to upper end limit
OBJECT_BINARY_VALUE:413 | 47818 | Z4_UP_BV | 5 | 413 | Write "1" to send group to upper end limit
OBJECT_BINARY_VALUE:513 | 47818 | Z5_UP_BV | 5 | 513 | Write "1" to send group to upper end limit
OBJECT_BINARY_VALUE:613 | 47818 | Z6_UP_BV | 5 | 613 | Write "1" to send group to upper end limit
OBJECT_BINARY_VALUE:713 | 47818 | Z7_UP_BV | 5 | 713 | Write "1" to send group to upper end limit
OBJECT_BINARY_VALUE:813 | 47818 | Z8_UP_BV | 5 | 813 | Write "1" to send group to upper end limit
OBJECT_BINARY_VALUE:114 | 47818 | Z1_STOP_BV | 5 | 114 | Write "1" to stop group
OBJECT_BINARY_VALUE:214 | 47818 | Z2_STOP_BV | 5 | 214 | Write "1" to stop group
OBJECT_BINARY_VALUE:314 | 47818 | Z3_STOP_BV | 5 | 314 | Write "1" to stop group
OBJECT_BINARY_VALUE:414 | 47818 | Z4_STOP_BV | 5 | 414 | Write "1" to stop group
OBJECT_BINARY_VALUE:514 | 47818 | Z5_STOP_BV | 5 | 514 | Write "1" to stop group
OBJECT_BINARY_VALUE:614 | 47818 | Z6_STOP_BV | 5 | 614 | Write "1" to stop group
OBJECT_BINARY_VALUE:714 | 47818 | Z7_STOP_BV | 5 | 714 | Write "1" to stop group
OBJECT_BINARY_VALUE:814 | 47818 | Z8_STOP_BV | 5 | 814 | Write "1" to stop group
OBJECT_ANALOG_VALUE:100 | 47818 | Z1_BLIND_POSITION_AV | 2 | 100 | Write a value between 0 % and 100 % to move the blinds to the desired position
OBJECT_ANALOG_VALUE:200 | 47818 | Z2_BLIND_POSITION_AV | 2 | 200 | Write a value between 0 % and 100 % to move the blinds to the desired position
OBJECT_ANALOG_VALUE:300 | 47818 | Z3_BLIND_POSITION_AV | 2 | 300 | Write a value between 0 % and 100 % to move the blinds to the desired position
OBJECT_ANALOG_VALUE:400 | 47818 | Z4_BLIND_POSITION_AV | 2 | 400 | Write a value between 0 % and 100 % to move the blinds to the desired position
OBJECT_ANALOG_VALUE:500 | 47818 | Z5_BLIND_POSITION_AV | 2 | 500 | Write a value between 0 % and 100 % to move the blinds to the desired position
OBJECT_ANALOG_VALUE:600 | 47818 | Z6_BLIND_POSITION_AV | 2 | 600 | Write a value between 0 % and 100 % to move the blinds to the desired position
OBJECT_ANALOG_VALUE:700 | 47818 | Z7_BLIND_POSITION_AV | 2 | 700 | Write a value between 0 % and 100 % to move the blinds to the desired position
OBJECT_ANALOG_VALUE:800 | 47818 | Z8_BLIND_POSITION_AV | 2 | 800 | Write a value between 0 % and 100 % to move the blinds to the desired position
OBJECT_ANALOG_VALUE:101 | 47818 | Z1_BLIND_ANGLE_AV | 2 | 101 | Write a value between 0° and 90° or -90° and 90° to move the blinds to the desired angle
OBJECT_ANALOG_VALUE:201 | 47818 | Z2_BLIND_ANGLE_AV | 2 | 201 | Write a value between 0° and 90° or -90° and 90° to move the blinds to the desired angle
OBJECT_ANALOG_VALUE:301 | 47818 | Z3_BLIND_ANGLE_AV | 2 | 301 | Write a value between 0° and 90° or -90° and 90° to move the blinds to the desired angle
OBJECT_ANALOG_VALUE:401 | 47818 | Z4_BLIND_ANGLE_AV | 2 | 401 | Write a value between 0° and 90° or -90° and 90° to move the blinds to the desired angle
OBJECT_ANALOG_VALUE:501 | 47818 | Z5_BLIND_ANGLE_AV | 2 | 501 | Write a value between 0° and 90° or -90° and 90° to move the blinds to the desired angle
OBJECT_ANALOG_VALUE:601 | 47818 | Z6_BLIND_ANGLE_AV | 2 | 601 | Write a value between 0° and 90° or -90° and 90° to move the blinds to the desired angle
OBJECT_ANALOG_VALUE:701 | 47818 | Z7_BLIND_ANGLE_AV | 2 | 701 | Write a value between 0° and 90° or -90° and 90° to move the blinds to the desired angle
OBJECT_ANALOG_VALUE:801 | 47818 | Z8_BLIND_ANGLE_AV | 2 | 801 | Write a value between 0° and 90° or -90° and 90° to move the blinds to the desired angle